## Rev1
BOILLER DESK LOGBOOK CUM LOGSHEET |  |  | Unit | Date |  |  | Ex..24-04-2024
|  |  |  | Name |  |  | Ex. gjfjtdk
|  |  |  | Shift |  |  | I - Shift |  | II - Shift |  | III - Shift |  | I - Shift |  | II - Shift |  | III - Shift
SN | Boiler Desk Parameter |  | UNIT | Normal Value | Alarm Value | Trip Value | Shift Start | Shift End | Shift Start | Shift End | Shift Start | Shift End | Shift Start | Shift End | Shift Start | Shift End | Shift Start | Shift End
1 | Load |  | MW
2 | MS Pressure |  | Bar | 40-135
3 | MS Temp. |  | °C | 480-538
4 | MS Flow |  | TPH | 100-375
5 | FW Flow(T/Hr) |  | TPH | 100-385
6 | Drum Pr.(Bar) |  | Bar | 50-150
7 | Drum L (mmwc) |  | mmwc | 25-50
8 | HRH Pr.(Bar) |  | Bar | 6-35
9 | HRH Temp.(“C) |  | °C | 480-537
| CRH Pressure |  | Bar | 6-38
10 | CRH Temp. |  | °C | 300-355
Steam & FW Temp
5 | ECO I/L |  | °C | 180-242
6 | ECO O/L |  | °C | 200-340
7 | After SH2 |  | °C | 255-350
8 | After SH3 |  | °C | 300-357
9 | After SH4 |  | °C | 350-490
10 | After SH5 |  | °C | 450-538
11 | After RH1 |  | °C | 300-460
12 | After RH2 |  | °C | 450-537 |  | 560
SH Attem. Stage 1
13 | Temp at I/L |  | °C | 300-340
14 | Temp at O/L |  | °C | 355-425
15 | Flow (Kg/S) |  | Kg/S | 0-11
SH Attem. Stage 2
16 | Temp at I/L |  | °C | 300-400
17 | Temp at O/L |  | °C | 400-490
18 | Flow (Kg/S) |  | Kg/S | 0-8
RH Attem.
19 | Temp at I/L |  | °C | 300-340
20 | Temp at O/L |  | °C | 380-442 |  | 560
21 | Flow (Kg/S) |  | Kg/S | 0-8
Metal Temp/PRDS
22 | Drum Left |  | °C | 250-360
23 | Drum Right |  | °C | 250-360
24 | SH1 |  | °C | 300-420
25 | SH4 |  | °C | 450-530
26 | SH5 |  | °C | 480-550
27 | RH2 |  | °C | 480-550
28 | PRDS Pressure |  | °C | 16.8-17.2
28 | PRDS Temp. |  | °C | 320-335
29 | PRDS Flow. |  | Kg/S | 1-8
30 | Atom.stm Pressure |  | Bar | 10-16
31 | Inst. Air Pressure |  | Bar | 5.6-6.5 | 5.5
ID FAN
32 | Current | A | Amp | 40-90 |  | 95
|  | B | Amp | 40-90 |  | 95
33 | Speed | A | RPM | 350-680
|  | B | RPM | 350-680
34 | Scoop | A | % | 15-70
|  | B | % | 15-70
35 | IGV % | A | % | 0-100
|  | B | % | 0-100
37 | LOP (R/SB) | A | 1 | R
|  |  | 2 | S/B
|  | B | 1 | R
|  |  | 2 | S/B
38 | ID FAN A Sump Oil Temp | A | °C | 85-98 | 135 | 140
39 | ID FAN B Sump Oil Temp | B | °C | 85-98 | 135 | 140
PA FAN A
40 | Current | A | Amp | 50-115 |  | 122
|  | B | Amp | 50-115 |  | 122
43 | IGV % | A | % | 20-80
|  | B | % | 20-80
44 | LOP (R/SB) | A | 1 | S/B
|  |  | 2 | R
|  | B | 1 | S/B
|  |  | 2 | R
45 | Dis. Pressure | A | mbar | 100-180
|  | B | mbar | 100-180
46 | Header Pressure |  | mbar | 90-160 |  | 40
47 | Flow Pressure |  | Kg/S | 18-26 | 15 | 7.5
SA FAN
48 | Current | A | Amp | 50-82 |  | 86
|  | B | Amp | 50-82 |  | 86
51 | IGV % | A | % | 10-80
|  | B | % | 10-60
52 | DISH.Pr. | A | mbar | 60-120
|  | B | mbar | 60-120
53 | SA Flow |  | Kg/S | 32-74
54 | HDR Pressure |  | mbar | 40-90 |  | 15
FA FAN
55 | FA Fan Current | A | Amp | 125-180 |  | 250
|  | B | Amp | 125-180 |  | 250
|  | C | Amp | 125-180 |  | 250
56 | FA Hdr. Pressure |  | Bar | 0.35-0.45 | 0.30 | 0.25
Ash Cooler Fan A
57 | Current |  | Amp | 130-230 |  | 250
58 | Brg. Vibration |  | us | 0-30
59 | Brg Temp | DE | °C | 50-65
|  | NDE | °C | 50-65
Air/FG Parameter
60 | BMCR % |  | % | 25-92
61 | O2% Before TAPH (Lignite # HFO) |  | % | 3.6-8.6 # 12-14
62 | TotaI Airflow |  | Kg/S | 72-132
63 | Lignite Flow | A | TPH | 10-55
|  | B | TPH | 10-55
64 | Bed Temp |  | °C | 660-850
65 | Bed Pr. |  | mbar | 50-120
| PAWB pr. |  | mbar | 90-160
66 | 2nd pass l/L Pr |  | mbar | -0.5/-2.5
67 | 2nd pass O/L Pr |  | mbar | -5/-10
FG Temp.
68 | After 2nd pass |  | °C | 180-270
69 | After TAPH |  | °C | 140-150
70 | After ESP |  | °C | 135-150
71 | At Chimney |  | °C | 132-140
FG Analysis
72 | O2 at chimney |  | %
73 | SOX |  | (mg/m3) | 30-50
74 | NOX |  | (mg/m3)
75 | CO |  | (mg/m3)
76 | Opacity |  | (mg/m3)
Metal Temp / PRDS
77 | Drum Left |  | °C | 250-400
78 | Drum Right |  | °C | 250-400
79 | SH1 |  | °C | 300-420
80 | SH4 |  | °C | 460-540
81 | SH5 |  | °C | 480-550
82 | RH2 |  | °C | 480-550
HFO Parameter
87 | HFO Tr.Pump Dis Pressure | A | Bar | 14-16
|  | B | Bar | 14-16
88 | HFO Temp at Heater O/L |  | °C | 130-140
89 | HFO Flow |  | TPH | 0-10
90 | Oil Pr. Burner I/L |  | Bar | 13-15
91 | Oil Temp Burner I/L |  | °C | 120-130
92 | HOt Water Pump Starus (R/SB/NA) | A |  | R
|  | B |  | S/B
|  | C |  | R
Cyclone A
93 | Downcomer Pressure |  | mbar | 0/-5
94 | Inlet Temp |  | °C | 650-850
95 | Outlet Temp | 1 | °C | 650-830
|  | 2 | °C | 650-830
|  | 3 | °C | 650-830
Cyclone B
96 | Downcomer Pressure |  | mbar | 0/-5
97 | Inlet Temp |  | °C | 650-850
98 | Outlet Temp | 1 | °C | 650-830
|  | 2 | °C | 650-830
|  | 3 | °C | 650-830
99 | Lime Feeding Hrs |  | Hrs
100 | G.F. Current | A | Amp | 11-14 |  | 20
|  | B | Amp | 11-14 |  | 20
101 | Lig. Dra. Current | A | Amp | 8-12
|  | B | Amp | 8-12
102 | RALF Current | AA | Amp | 6-8
|  | AB | Amp | 6-8
|  | BA | Amp | 6-8
|  | BB | Amp | 6-8
PA Fan A
103 | Motor Brg.Temp | DE | °C |  | 70 | 85
|  | NDE | °C |  | 70 | 85
104 | Fan Bearing Temp | DE | °C |  | 70 | 85
|  | NDE | °C |  | 70 | 85
105 | Brg. Vibration | DE | °C
|  | NDE | °C
106 | Motor Wind. Temp | Max. | °C |  | 115 | 120
PA Fan B
107 | Motor Brg.Temp | DE | °C |  | 70 | 85
|  | NDE | °C |  | 70 | 85
108 | Fan Bearing Temp | DE | °C |  | 70 | 85
|  | NDE | °C |  | 70 | 85
109 | Brg. Vibration | DE | °C
|  | NDE | °C
110 | Motor Wind. Temp | Max. | °C |  | 115 | 120
SA Fan A
111 | Motor Brg.Temp | DE | °C |  | 70 | 85
|  | NDE | °C |  | 70 | 85
112 | Fan Bearing Temp | DE | °C |  | 70 | 85
|  | NDE | °C |  | 70 | 85
113 | Brg. Vibration | DE | °C
|  | NDE | °C
114 | Motor Wind. Temp | Max. | °C |  | 115 | 120
SA Fan B
115 | Motor Brg.Temp | DE | °C |  | 70 | 85
|  | NDE | °C |  | 70 | 85
116 | Fan Bearing Temp | DE | °C |  | 70 | 85
|  | NDE | °C |  | 70 | 85
117 | Brg. Vibration | DE | °C
|  | NDE | °C
118 | Motor Wind. Temp | Max. | °C |  | 115 | 120
ID Fan A
119 | Motor Brg.Temp | DE | °C |  | 70 | 85
|  | NDE | °C |  | 70 | 85
120 | Fan Bearing Temp | DE | °C |  | 70 | 85
|  | NDE | °C |  | 70 | 85
121 | Brg. Vibration | DE | °C
|  | NDE | °C
122 | Motor Wind. Temp | Max. | °C |  | 115 | 120
ID Fan B
123 | Motor Brg.Temp | DE | °C |  | 70 | 85
|  | NDE | °C |  | 70 | 85
124 | Fan Bearing Temp | DE | °C |  | 70 | 85
|  | NDE | °C |  | 70 | 85
125 | Brg. Vibration | DE | °C
|  | NDE | °C
126 | Motor Wind. Temp | Max. | °C |  | 115 | 120
ID Fan voith scoop Local Parameter
1 | ID A Voith LOP Pr |  | Bar | 0.2 |  | 0.020
2 | Oil Level A |  | % | 50
3 | Oil Temp (In/Out) A |  | °C | 75/85
4 | DP - Voith A filter |  | Bar
5 | ID A Voith LOP Pr |  | Bar
6 | Oil Level B |  | %
7 | Oil Temp (In/Out) B |  | °C
8 | DP - Voith B filter |  | Bar
Bed Material Cycle Taken
| L Valve A1 |  | Time
| L Valve A2 |  | Time
| L Valve B1 |  | Time
| L Valve B2 |  | Time
EQUIPMENT'S TOTAL RUNNING HOURS AT SHIFT END
1 | ID FAN A
2 | IDF-A LOP 1
3 | IDF-A LOP 2
4 | ID FAN B
5 | IDF-B LOP 1
6 | IDF-B LOP 2
7 | PA FAN A
8 | PAF-A LOP 1
9 | PAF-A LOP 2
10 | PA FAN B
11 | PAF-B LOP 1
12 | PAF-B LOP 2
13 | SA FAN A
14 | SA FAN B
15 | FA FAN A
16 | FA FAN B
17 | FA FAN C
18 | Ash Cooler Fan A
19 | Ash Cooler Fan B
20 | Hot Water Pump A
21 | Hot Water Pump B
22 | Hot Water Pump C
23 | HFO TR.Pump A
24 | HFO TR.Pump B
25 | GRA.FEEDER .A
26 | LIG.DRAG. A
27 | RALF AA
28 | RALF AA
29 | GRA.FEEDER B
30 | LIG.DRAG. B
31 | RALF BA
32 | RALF BB
NA Equipments:
Important Activity carried out during shift: (I-Shift)
Important Activity carried out during shift: (II-Shift)
Important Activity carried out during shift: (III-Shift)